## Results
Attribute | Report | Room_PHAERO_2_EAST | Room_PHAERO_2_INTERNAL_ONLY | Room_PHAERO_2_NORTH | Room_PHAERO_2_SOUTH | Room_PHAERO_2_WEST
CO2 | PEAK-SUMMARY | 669.2 | 648.5 | 668.5 | 652.1 | 652.1
DRYVENTCOOL | PEAK-SUMMARY | 393.3 | 299.2 | 446.3 | 455.5 | 398.1
DRYVENTCOOL_2NDSNAP | PEAK-SUMMARY | -391.2 | -265.7 | -446.2 | -414 | -329.2
MAXHEATREM | PEAK-SUMMARY | 495.9 | 437.4 | 548.1 | 589.2 | 501.7
MAXHEATREM_2NDSNAP | PEAK-SUMMARY | 495.9 | 437.4 | 548.1 | 589.2 | 501.7
MAXSENSREM | PEAK-SUMMARY | 388.6 | 292.5 | 443.9 | 453.3 | 394.5
MULTIPLICITY | PEAK-SUMMARY | 2 | 2 | 2 | 2 | 2
OTHERSUPAIRFLOW | PEAK-SUMMARY | 1.633 | 1.633 | 1.633 | 1.633 | 1.633
OTHERSUPAIRTEMP | PEAK-SUMMARY | 26.48 | 21.12 | 25.09 | 21.61 | 21.61
PEAK | PEAK-SUMMARY | 495.9 | 437.4 | 548.1 | 589.2 | 501.7
PEAK_TIME | PEAK-SUMMARY | 3961579428 | 3961558081 | 3961584000 | 3961558800 | 3961558800
PEAK_TIME_2NDSNAP | PEAK-SUMMARY | 3961579428 | 3961558081 | 3961584000 | 3961558800 | 3961558800
PEAK_TYPE | PEAK-SUMMARY | MAXHEATREM | MAXHEATREM | MAXHEATREM | MAXHEATREM | MAXHEATREM
PEAK_VAR | PEAK-SUMMARY | FALSE | FALSE | FALSE | FALSE | FALSE
PPD | PEAK-SUMMARY | 5.002 | 6.565 | 5.337 | 5.07 | 5.371
QINTW | PEAK-SUMMARY | -374.7 | -149 | -352.5 | -394.5 | -230.3
QL_A | PEAK-SUMMARY | 5.471 | -3.009 | 1.155 | -6.804 | -4.071
QVENTIL | PEAK-SUMMARY | -391.2 | -265.7 | -446.2 | -414 | -329.2
QVENTIL_2NDSNAP | PEAK-SUMMARY | -391.2 | -265.7 | -446.2 | -414 | -329.2
QWCB | PEAK-SUMMARY | -431.9 | -255.1 | -494.2 | -579 | -376
QWIND | PEAK-SUMMARY | 523.9 | 0 | 631.5 | 729.1 | 272.2
Q_COOL | PEAK-SUMMARY | 0 | 0 | 0 | 0 | 0
Q_COOL_2NDSNAP | PEAK-SUMMARY | 0 | 0 | 0 | 0 | 0
Q_DRYVENT | PEAK-SUMMARY | -391.2 | -265.7 | -446.2 | -414 | -329.2
Q_DRYVENT_2NDSNAP | PEAK-SUMMARY | -391.2 | -265.7 | -446.2 | -414 | -329.2
Q_EQUIP | PEAK-SUMMARY | 200.3 | 200.3 | 198.3 | 200.3 | 200.3
Q_HEAT | PEAK-SUMMARY | 0 | 1.627e-19 | 0 | 0 | 0
Q_LIGHT | PEAK-SUMMARY | 239.7 | 240.1 | 233.9 | 238.7 | 239.4
Q_LOSS | PEAK-SUMMARY | 0 | 0 | 0 | 0 | 0
Q_OCC | PEAK-SUMMARY | 233.4 | 236.3 | 231.1 | 236 | 236
RELHUM | PEAK-SUMMARY | 51.67 | 63.81 | 49.19 | 55.22 | 59.7
RETAIRFLOW | PEAK-SUMMARY | -52.7801 | -53.0389 | -52.6298 | -52.6465 | -52.8803
ROOMUNITCOOL | PEAK-SUMMARY | 0 | 0 | 0 | 0 | 0
ROOMUNITCOOL_2NDSNAP | PEAK-SUMMARY | 0 | 0 | 0 | 0 | 0
SETPOINT | PEAK-SUMMARY | 24 | 24 | 24 | 24 | 24
SUPAIRFLOW | PEAK-SUMMARY | 53.9155 | 53.8654 | 53.9155 | 53.8738 | 53.8738
SUPAIRFLOW_2NDSNAP | PEAK-SUMMARY | 53.9155 | 53.8654 | 53.9155 | 53.8738 | 53.8738
SUPAIRTEMP | PEAK-SUMMARY | 17.01 | 17.01 | 17.01 | 17.01 | 17.01
SUPAIRTEMP_2NDSNAP | PEAK-SUMMARY | 17.01 | 17.01 | 17.01 | 17.01 | 17.01
TAIR | PEAK-SUMMARY | 22.94 | 21.04 | 23.78 | 23.29 | 22
TAIR_2NDSNAP | PEAK-SUMMARY | 22.94 | 21.04 | 23.78 | 23.29 | 22
TOP | PEAK-SUMMARY | 23.02 | 20.97 | 23.96 | 23.37 | 22.01
DRYVENTCOOL | ZONE-SUMMARY | 8.0265 | 6.1061 | 9.1082 | 9.2959 | 8.1245
H_T_AIR_HI | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
H_T_AIR_LO | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
H_T_OP_HI | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
H_T_OP_LO | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
MAXAIRAGE | ZONE-SUMMARY | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
MAXCO2 | ZONE-SUMMARY | 669.3 | 669.3 | 669.3 | 669.3 | 669.3
MAXEXHAIRFLOW | ZONE-SUMMARY | 1.0852 | 1.0872 | 1.0829 | 1.0821 | 1.084
MAXHEATREM | ZONE-SUMMARY | 10.1204 | 8.9265 | 11.1857 | 12.0245 | 10.2388
MAXHEATSUP | ZONE-SUMMARY | 0 | 8.0449 | 0 | 0 | 0
MAXPPD | ZONE-SUMMARY | 6.589 | 7.708 | 5.663 | 5.459 | 6.159
MAXRELHUM | ZONE-SUMMARY | 64.39 | 67.47 | 62.4 | 61.74 | 63.42
MAXSOLAR | ZONE-SUMMARY | 12.7082 | 0 | 17.8714 | 22.0816 | 11.6776
MAXSUPAIRFLOW | ZONE-SUMMARY | 1.1005 | 1.1005 | 1.1005 | 1.1005 | 1.1005
MINRELHUM | ZONE-SUMMARY | 51.58 | 56.33 | 49.19 | 48.78 | 51.43
MULTIPLICITY | ZONE-SUMMARY | 2 | 2 | 2 | 2 | 2
NET_FLOOR_AREA | ZONE-SUMMARY | 49 | 49 | 49 | 49 | 49
OCCUPANCY | ZONE-SUMMARY | 11 | 11 | 11 | 11 | 11
OCC_HOURS | ZONE-SUMMARY | 29.37 | 29.37 | 29.37 | 29.37 | 29.37
PDH | ZONE-SUMMARY | 1.557 | 1.88 | 1.517 | 1.522 | 1.542
ROOMUNITCOOL | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
ROOMUNITCOOLEN | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
ROOMUNITCOOLENAREA | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
ROOMUNITHEAT | ZONE-SUMMARY | 3.8469e-18 | 12.502 | 8.698e-18 | 5.2449e-18 | 4.5531e-18
ROOMUNITHEATEN | ZONE-SUMMARY | 0 | 0.2698 | 4.023e-19 | 0 | 0
ROOMUNITHEATENAREA | ZONE-SUMMARY | 0 | 0.0055061 | 8.2102e-21 | 0 | 0
TAIRMAX | ZONE-SUMMARY | 22.98 | 21.55 | 23.78 | 23.92 | 23.05
TAIRMIN | ZONE-SUMMARY | 20.63 | 20.06 | 21.18 | 21.39 | 20.93
TATMAXSUPAIRFLOW | ZONE-SUMMARY | 17.01 | 17.01 | 17.01 | 17.01 | 17.01
TOPMAX | ZONE-SUMMARY | 23.08 | 21.55 | 23.97 | 24.1 | 23.14
TOPMIN | ZONE-SUMMARY | 21 | 20.38 | 21.72 | 22.37 | 21.3
UNMET_COOL | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0
UNMET_HEAT | ZONE-SUMMARY | 0 | 0 | 0 | 0 | 0